## Français
Tableau de calcul des Fils de Cuivre | [7 empty] | Tableau déniché par Charles Lebosse et traduit et adapté par Phil le rampant.
Plus bas, vous trouverez trois cases à remplir avec les données de votre fil : Jauge AWG, longueur, intensité | [7 empty] | Voir les copyrights sur la feuille Anglais(US)
Le tableau vous retournera sa résistance, son poids, la chute de tension et l'élévation de température.
Jauge | Diamètre | Section | Résistance (W) | Poids (kg) | I Fusion (A) | I Max (A) | Rupture (kg) |  | Diamètre
AWG (*) | mm | mm² | pour 100 m | pour 100 m |  | en faisceau |  |  | millièmes de pouces
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | <== Notes | REFERENCE US
-4 | 11.68 | 107.1459 | 0.016117 | 95.0528 | 3180.9145 | 214.2387 | 2821.2242 | 1. La norme American Wire Gauje, est aussi appellée Birmingham & Stubbs Jauge (B&S) | 460
-3 | 10.4 | 84.9487 | 0.020329 | 75.3609 | 2672.6232 | 169.8552 | 2236.7559 | 2. Le diamètre est une conversion des millièmes de pouces US, arrondi à 2 décimales. | 409.6418
-2 | 9.27 | 67.4915 | 0.025587 | 59.8741 | 2249.0926 | 134.9496 | 1777.098 | Cette donnée concerne le fil rigide. /!\ les fils "stranded" (traduction impossible) sont 10 à 15 % plus minces. | 364.7966
0 | 8.25 | 53.4562 | 0.032305 | 47.4228 | 1888.2898 | 106.8858 | 1407.537 |  | 324.8607
2 | 6.54 | 33.5927 | 0.051406 | 29.8013 | 1332.7674 | 67.1688 | 884.5195 | 4. La résistance est donnée en ohms pour 100 m de fil. | 257.6263
4 | 5.19 | 21.1556 | 0.081628 | 18.7678 | 942.1906 | 42.3006 | 557.0403 | 5. Le poids est donné en kg pour 100 m de fil nu. Ajouter environ 25% pour l'isolant. | 204.3069
6 | 4.12 | 13.3317 | 0.12953 | 11.827 | 666.3978 | 26.6567 | 351.0317 | 6. Le courant de fusion fait fondre le fil. Non ? Si. C'est une estimation qui ne tient pas compte | 162.0228
8 | 3.26 | 8.3469 | 0.20689 | 7.4048 | 469.0446 | 16.6897 | 219.7795 | de la température ambiante, des sources de chaleur proches, etc. | 128.4899
10 | 2.59 | 5.2685 | 0.32777 | 4.6739 | 332.1524 | 10.5344 | 138.7239 | 7. Courant maxi (recommandation FAA) pour un fil environné d'autres fils. Oui, t'as raison, c'est un faisceau ! | 101.8971
12 | 2.05 | 3.3006 | 0.5232 | 2.9281 | 233.8937 | 6.5996 | 86.908 | 8. Tu tires dessus de ça, et ça casse. | 80.8081
14 | 1.63 | 2.0867 | 0.82756 | 1.8512 | 165.8323 | 4.1724 | 54.9449 |  | 64.0837
16 | 1.29 | 1.307 | 1.3213 | 1.1595 | 116.7541 | 2.6133 | 34.4137 |  | 50.8207
18 | 1.02 | 0.81713 | 2.1134 | 0.7249 | 82.0896 | 1.6339 | 21.5155 |  | 40.3027
20 | 0.81 | 0.5153 | 3.3512 | 0.45714 | 58.0919 | 1.0303 | 13.5682 |  | 31.9615
22 | 0.64 | 0.3217 | 5.368 | 0.28539 | 40.7998 | 0.64324 | 8.4706 |  | 25.3466
24 | 0.51 | 0.20428 | 8.4534 | 0.18123 | 29.023 | 0.40846 | 5.3789 |  | 20.1008
26 | 0.4 | 0.12566 | 13.7421 | 0.11148 | 20.1594 | 0.25127 | 3.3088 |  | 15.9406
28 | 0.32 | 0.080425 | 21.472 | 0.071348 | 14.4249 | 0.16081 | 2.1176 |  | 12.6415
30 | 0.25 | 0.049087 | 35.1798 | 0.043547 | 9.9609 | 0.09815 | 1.2925 |  | 10.0252
32 | 0.2 | 0.031416 | 54.9684 | 0.02787 | 7.1274 | 0.062816 | 0.8272 |  | 7.9503
34 | 0.16 | 0.020106 | 85.8881 | 0.017837 | 5.1 | 0.040202 | 0.52941 |  | 6.3049
36 | 0.13 | 0.013273 | 130.1027 | 0.011775 | 3.7351 | 0.02654 | 0.34949 |  | 5
38 | 0.1 | 0.007854 | 219.8735 | 0.0069675 | 2.5199 | 0.015704 | 0.2068 |  | 3.9652
40 | 0.08 | 0.0050265 | 343.5524 | 0.0044592 | 1.8031 | 0.010051 | 0.13235 |  | 3.1445
Utilisez la touche [Tab] pour aller aux cases à renseigner.
* Dans ce tableau, on utilise
|  |  |  | Jauge du fil (en American Wire Gauge ou AWG*) | 16 | AWG | -4 pour la jauge AWG 0000
-3 pour la jauge AWG 000
|  |  |  | Longueur (m) | 21.54 | m | -2 pour la jauge AWG 00
|  |  |  | Intensité (en ampères, A) | 8 | amperes
|  |  |  | Résistance (en Ohms) | 0.2846 | ohms
|  |  |  | Poids (kg) | 0.24975 | kg | Ajouter 25% pour l'isolant (approximation)
|  |  |  | Chute de tension (V) | 2.2768 | volts
|  |  |  | Section (en mm²) | 1.307 | mm²
|  |  |  | Elévation de température (en petit faisceau) | 10.5394 | °F
|  |  |  | valable pour les jauges AWG12 à AWG30, | 5.8552 | °C
et en-dessous de 100 Ampères SEULEMENT,
isolant PVC épaisseur 0,4 mm.

## Anglais (US)
COPPER WIRE TABLE
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Gauge | Diameter | Area | Resistance | Weight | Fusing | Bundle | Breaking
AWG | mils | sq. inches | ohms | Pounds | Current | Current | pounds
(*)
-4 | 460 | 0.16619 | 0.049091 | 639.9987 | 3182.5487 | 214.3854 | 6232.1344
-3 | 409.6418 | 0.13179 | 0.061903 | 507.542 | 2674.5132 | 170.0154 | 4942.3073
-2 | 364.7966 | 0.10452 | 0.078058 | 402.4991 | 2247.5763 | 134.8283 | 3919.4279
0 | 324.8607 | 0.082887 | 0.09843 | 319.1963 | 1888.7921 | 106.9237 | 3108.2476
2 | 257.6263 | 0.052128 | 0.15651 | 200.7445 | 1333.9008 | 67.245 | 1954.7961
4 | 204.3069 | 0.032784 | 0.24886 | 126.2495 | 942.0261 | 42.2908 | 1229.3834
6 | 162.0228 | 0.020618 | 0.3957 | 79.3991 | 665.2767 | 26.5969 | 773.1668
8 | 128.4899 | 0.012967 | 0.62919 | 49.9346 | 469.8311 | 16.727 | 486.2494
10 | 101.8971 | 0.0081548 | 1.0005 | 31.4042 | 331.8036 | 10.5197 | 305.8052
12 | 80.8081 | 0.0051286 | 1.5908 | 19.7503 | 234.326 | 6.6159 | 192.3228
14 | 64.0837 | 0.0032254 | 2.5294 | 12.4211 | 165.4855 | 4.1608 | 120.953
16 | 50.8207 | 0.0020285 | 4.022 | 7.8117 | 116.869 | 2.6167 | 76.0681
18 | 40.3027 | 0.0012757 | 6.3952 | 4.9128 | 82.5351 | 1.6457 | 47.8397
20 | 31.9615 | 0.00080231 | 10.1687 | 3.0897 | 58.2879 | 1.035 | 30.0867
22 | 25.3466 | 0.00050458 | 16.1689 | 1.9431 | 41.164 | 0.65091 | 18.9217
24 | 20.1008 | 0.00031733 | 25.7096 | 1.222 | 29.0708 | 0.40936 | 11.9
26 | 15.9406 | 0.00019957 | 40.8799 | 0.76855 | 20.5303 | 0.25745 | 7.484
28 | 12.6415 | 0.00012551 | 65.0016 | 0.48335 | 14.4989 | 0.16191 | 4.7067
30 | 10.0252 | 7.8935e-05 | 103.3566 | 0.30398 | 10.2394 | 0.10183 | 2.9601
32 | 7.9503 | 4.9643e-05 | 164.3434 | 0.19118 | 7.2313 | 0.064039 | 1.8616
34 | 6.3049 | 3.1221e-05 | 261.3162 | 0.12023 | 5.1069 | 0.040275 | 1.1708
36 | 5 | 1.9635e-05 | 415.509 | 0.075614 | 3.6066 | 0.025329 | 0.73631
38 | 3.9652 | 1.2349e-05 | 660.6852 | 0.047554 | 2.547 | 0.01593 | 0.46307
40 | 3.1445 | 7.7661e-06 | 1050.5306 | 0.029907 | 1.7988 | 0.010018 | 0.29123
(*) Use -4 for 0000 gauge, -3 for 000 gauge, -2 for 00 gauge
Wire Gauge: |  |  |  |  | 12 | AWG
Wire Run Length (feet): |  |  |  |  | 327 | feet
Wire Current (amperes): |  |  |  |  | 24 | amperes
Wire Resistance (ohms) |  |  |  |  | 0.52019 | ohms
Wire Weight (pounds) |  |  |  |  | 6.4583 | pounds
Voltage drop (volts) |  |  |  |  | 12.4845 | volts
Wire Area (square mils) |  |  |  |  | 5.1286 | mils
APPROXIMATE Temp Rise (in a small bundle): |  |  |  |  | 32.1408 | °F
Valid For #12 through #30, less than 100 amps ONLY. |  |  |  |  | 17.856 | °C
PVC Insulation 15 mils thick.
1. Gauge is American Wire Gauge, sometimes called the Birmingham and Stubbs gauge (B&S gauge)
2 Diameter is the diameter of the wire itself in thousandths of an inch. Values shown are for
SOLID copper wire. Stranded wire will generally be 10% to 15% thicker.
3. Area is the cross sectional area of the wire in square inches. Note that for smaller wire sizes that
the exponential notation is used. For example, AWG 38 wire has an area of 1.24E-5, which is
0.0000124 square inches.
4. Resistance is the resistance in ohms of 1000 feet of wire. To get the resistance per foot, simply
divide the listed number by 1000.
5. Weight is the weight in pounds of 1000 feet of bare wire. To estimate the weight with insulation,
add approximately 25%.
6. Fusing is the current in amperes at which the wire will melt. Note that this is only an approximation
and ambient temperature, proximity to other heat sources, and other factors have not been considered.
7. Bundle is the recommended maximum current for any wire in a small bundle with other wires.
(Compiled from FAA documents and other sources.)
8. Break is the dead-weight breaking strength in pounds.
Brought to you courtesy of RST Engineering, Grass Valley CA 95945 530.272.2203 sales@rst-engr.com